- SS-35* - Corrosion resistant, combination eye wash/shower safety station with ABS plastic shower head, ABS plastic bowl, cast aluminum powder coated flag handle, PVC floor flange, 2” IPS Schedule 80 PVC pipe and fittings, 1” IPS and ½” IPS U.S. made PVC coated brass stay open ball valves, and polished stainless steel pull rod.  Unit shall have (2) polypropylene ‘FS Plus’ spray heads with integral “flip-top” dust covers, filters, and 3.2-GPM flow control orifices mounted on a PVC coated brass head assembly.  Unit shall include ANSI compliant sign.

- Performance:  Unit shall meet or exceed ANSI Z358.1 – 2009, and come with a full 2-year warranty.

- Fixture:  Guardian Equipment G1993