- TMV -10 – Thermostatic mixing valve (factory set to 85°F) for single emergency eye or eye/face wash.  Unit shall include a built-in cold water bypass, rough bronze finish, solid bimetal thermostat, locking temperature regulator with high temperature limit stop factory set for 90°F, integral check stops, and dial thermometer. Unit shall be mounted in a recessed 16 gauge type 304 stainless steel cabinet with #4 brushed satin finish, with door and lock.

- Performance:  Unit shall have a flow range of 0.5 GPM to 6.5 GPM with a maximum pressure loss of 30 PSI and come with a full 2-year warranty.

- Quality Assurance: Unit shall be certified to ASSE 1071. Unit shall be certified to meet Low Lead requirements of wetted surface area containing less than 0.25% lead by weight.

- Fixture:  Guardian G3607LF

Distributed by:

Safety Emporium

PO Box 1003

Blackwood, NJ 08012

Ph: (866) 326-5412 toll-free

Fax: (856) 553-6154

esupport@safetyemporium.com

www. safetyemporium.com