- TMV - 4 – Thermostatic mixing valve (factory set to 85 degrees) for single emergency eye wash.  Unit shall include a built-in cold water by-pass, rough bronze finish, solid bimetal thermostat, locking temperature regulator with limit stop factory set for 90 degrees, integral check stops, and dial thermometer

- Performance:  Unit shall have a flow range of 3-GPM to 44-GPM with a maximum pressure loss of 20-PSI and come with a full 1-year warranty.

- Quality Assurance: Unit shall be certified to ASSE 1071. Unit shall be certified to meet Low Lead requirements of wetted surface area containing less than 0.25% lead by weight.

- Fixture:  Guardian G3800LF