- DH-11* - Deck mounted, hand-held drench hose/eye wash with ½” IPS U.S. made chrome plated brass ball valve, powder coated cast aluminum flag handle, insulator handle, nylon deck flange with locator guide, and 8ft. PVC hose.  Unit shall have (2) polypropylene ‘GS Plus’ spray heads with integral “flip-top” dust covers, filters and 1.8-GPM flow control orifices mounted on a chrome plated brass eyewash assembly.  Unit shall include ANSI compliant sign.

- Performance:  Unit shall be fully factory assembled and hydrostatically tested to meet or exceed ANSI Z358.1 – 2009, and come with a full 2-year warranty.

- Fixture:  Guardian Equipment G5028