- EFBF-16* – Barrier Free, recessed wall mounted, eye/face wash with swing-down stainless steel drain pan.  Unit shall include all welded 16-gauge type 304 stainless steel construction, chrome plated brass eye/face wash supply fittings, ½” IPS brass rotating plug-type valve with Teflon coated O-ring seals. Supplied with in-line strainer to prevent debris from affecting the valve, and 2” IPS drain. Unit shall have (2) polypropylene ‘FS Plus’ spray heads with integral filters and 3.2-GPM flow control orifices.  Activate valve by rotating 90° from stored position.  Unit shall include ANSI compliant sign.

- Performance: Unit complies with ADA requirements for accessibility by handicapped persons. Unit shall be fully factory assembled and hydrostatically tested to meet or exceed ANSI Z358.1 – 2009, and come with a full 2-year warranty.

- Fixture: Guardian GBF1735DP